## STUDIO
Paramount Mix Development Plot 1 - Studio Apartment Lux Calculation | [15 empty] | Date : 20 Jun 2017
Building Description | Area A | Floor Height | Reflection Factor |  |  | Work Plane (H1) | Mounting Height (H2) | Utilization Factor (U) | Maintenance Factor (M) | Fixture Type | Lamp Lumens per Luminaire (F) | Lumens / Watts | Specified Illumination (E) | Calculated Number of Fixtures (Nc) = | Proposed No. of Fixture (N) | Design Illumination (Ei) =
| m² | m | Ceiling (%) | Wall (%) | Floor (%) | m | m | % | % |  | lm |  | lx | (A x E)/(F x U x M) |  | (N x F x U x M)/A
LEVEL 4
CAR PARK - Studio | 4000 | 3 | 0.7 | 0.3 | 0.1 | 0.8 | 2.85 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 238 | 202 | 72.114
LEVEL 5
CAR PARK - Studio | 7750 | 3 | 0.7 | 0.3 | 0.1 | 0.8 | 2.85 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 461 | 396 | 72.9662
LOBBY BLOCK A | 19.6 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 88.4694
LOBBY BLOCK B | 19.6 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 88.4694
STAIRCASE 4 BLOCK A | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 5 BLOCK A | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102
STAIRCASE 6 BLOCK B | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 7 BLOCK B | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102
LEVEL 6
CAR PARK - Studio | 7750 | 3 | 0.7 | 0.3 | 0.1 | 0.8 | 2.85 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 461 | 396 | 72.9662
LOBBY BLOCK A | 19.6 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 88.4694
LOBBY BLOCK B | 19.6 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 88.4694
STAIRCASE 4 BLOCK A | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 5 BLOCK A | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102
STAIRCASE 6 BLOCK B | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 7 BLOCK B | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102
LEVEL 7
CAR PARK - Studio | 7750 | 3 | 0.7 | 0.3 | 0.1 | 0.8 | 2.85 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 461 | 396 | 72.9662
LOBBY BLOCK A | 19.6 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 88.4694
LOBBY BLOCK B | 19.6 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 88.4694
STAIRCASE 4 BLOCK A | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 5 BLOCK A | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102
STAIRCASE 6 BLOCK B | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 7 BLOCK B | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102
LEVEL 8
CAR PARK | 11750 | 3 | 0.7 | 0.3 | 0.1 | 0.8 | 2.85 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 699 | 598 | 72.6761
LOBBY BLOCK A | 19.6 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 88.4694
LOBBY BLOCK B | 19.6 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 88.4694
STAIRCASE 4 BLOCK A | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 5 BLOCK A | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102
STAIRCASE 6 BLOCK B | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 7 BLOCK B | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 18W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102
LEVEL 9
FUNCTION AREA | 129.65 | 3.4 | 0.7 | 0.3 | 0.1 | 0.8 | 3 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 22 | 19 | 84.705
CORRIDOR BLOCK A | 114.36 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 20 | 21 | 106.1385
CORRIDOR BLOCK B | 114.36 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 20 | 21 | 106.1385
LOBBY BLOCK A | 18 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 96.3333
LOBBY BLOCK B | 18 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 96.3333
STAIRCASE 4 BLOCK A | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 20W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 5 BLOCK A | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 20W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102
STAIRCASE 6 BLOCK B | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 20W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 7 BLOCK B | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 20W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102
CORRIDOR BLOCK CENTER | 62.86 | 3.4 | 0.7 | 0.3 | 0.1 | 0.8 | 3 | 0.8 | 0.85 | 8W LED DOWNLIGHT | 850 | 85 | 100 | 11 | 12 | 110.3404
LEVEL 10
GYMNASIUM | 139.93 | 3.4 | 0.7 | 0.3 | 0.1 | 0.8 | 3 | 0.8 | 0.85 | 18W LED DOWNLIGHT | 1650 | 82.5 | 200 | 25 | 18 | 144.3293
CORRIDOR BLOCK A | 114.36 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 20 | 21 | 106.1385
CORRIDOR BLOCK B | 114.36 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 20 | 21 | 106.1385
LOBBY BLOCK A | 19.6 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 88.4694
LOBBY BLOCK B | 19.6 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 88.4694
STAIRCASE 4 BLOCK A | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 20W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 5 BLOCK A | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 20W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102
STAIRCASE 6 BLOCK B | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 20W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 7 BLOCK B | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 20W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102
LEVEL 11-26
CORRIDOR BLOCK A | 114.36 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 20 | 21 | 106.1385
CORRIDOR BLOCK B | 114.36 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 20 | 21 | 106.1385
LOBBY BLOCK A | 19.6 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 88.4694
LOBBY BLOCK B | 19.6 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 10W LED DOWNLIGHT | 850 | 85 | 100 | 3 | 3 | 88.4694
STAIRCASE 4 BLOCK A | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 20W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 5 BLOCK A | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 20W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102
STAIRCASE 6 BLOCK B | 16.35 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 20W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 87.3394
STAIRCASE 7 BLOCK B | 14 | 3.15 | 0.7 | 0.3 | 0.1 | 0.8 | 2.8 | 0.8 | 0.85 | 20W LED T8 Flourescent | 2100 | 116.6667 | 100 | 1 | 1 | 102

## aREA
| FFL | Area |  | Floor to Ceiling Height
|  | m² | ft² | m | ft
LEVEL 1
RETAIL 1 |  | 324 | 3487.536 |  | 0
RETAIL 2 |  | 115.31 | 1241.1968 |  | 0
RETAIL 3 |  | 102.97 | 1108.3691 |  | 0
RETAIL 3A |  | 124.6 | 1341.1944 |  | 0
RETAIL 5 |  | 105.92 | 1140.1229 |  | 0
RETAIL 6 |  | 124.61 | 1341.302 |  | 0
RETAIL 7 |  | 124.61 | 1341.302 |  | 0
RETAIL 8 |  | 124.61 | 1341.302 |  | 0
RETAIL 9 |  | 124.61 | 1341.302 |  | 0
RETAIL 10 |  | 113.68 | 1223.6515 |  | 0
RETAIL 11 |  | 117.39 | 1263.586 |  | 0
RETAIL 12 |  | 124.61 | 1341.302 |  | 0
RETAIL 12A |  | 113.89 | 1225.912 |  | 0
RETAIL 12B |  | 97.18 | 1046.0455 |  | 0
RETAIL 15 |  | 121.64 | 1309.333 |  | 0
RETAIL 16 |  | 130.15 | 1400.9346 |  | 0
RETAIL 17 |  | 130.15 | 1400.9346 |  | 0
RETAIL 18 |  | 181.29 | 1951.4056 |  | 0
RETAIL 19 |  | 169.25 | 1821.807 |  | 0
RETAIL 20 |  | 129.57 | 1394.6915 |  | 0
RETAIL 21 |  | 153.95 | 1657.1178 |  | 0
RETAIL 22 |  | 65.93 | 709.6705 |  | 0
RETAIL 23 |  | 124.6 | 1341.1944 |  | 0
RETAIL 23A |  | 130.15 | 1400.9346 |  | 0
RETAIL 25 |  | 130.17 | 1401.1499 |  | 0
RETAIL 26 |  | 124.6 | 1341.1944 |  | 0
RETAIL 27 |  | 124.24 | 1337.3194 |  | 0
RETAIL 28 |  | 124.6 | 1341.1944 |  | 0
RETAIL 29 |  | 125.2 | 1347.6528 |  | 0
RETAIL 30 |  | 200.5 | 2158.182 |  | 0
RETAIL 31 |  | 87.02 | 936.6833 |  | 0
RETAIL 32 |  | 87.44 | 941.2042 |  | 0
RETAIL 33 |  | 45.97 | 494.8211 |  | 0
RETAIL 33A |  | 90.91 | 978.5552 |  | 0
RETAIL 35 |  | 90.91 | 978.5552 |  | 0
RETAIL 36 |  | 87.02 | 936.6833 |  | 0
RETAIL 37 |  | 56 | 602.784 |  | 0
RETAIL 38 |  | 90.49 | 974.0344 |  | 0
RETAIL 39 |  | 119.14 | 1282.423 |  | 0
RETAIL 40 |  | 113.96 | 1226.6654 |  | 0
RETAIL 41 |  | 90.91 | 978.5552 |  | 0
RETAIL 42 |  | 90.91 | 978.5552 |  | 0
RETAIL 43 |  | 84.96 | 914.5094 |  | 0
RETAIL 43A |  | 38.52 | 414.6293 |  | 0
RETAIL 45 |  | 55.31 | 595.3568 |  | 0
RETAIL 46 |  | 87.02 | 936.6833 |  | 0
RETAIL 47 |  | 82.88 | 892.1203 |  | 0
RETAIL 48 |  | 83.34 | 897.0718 |  | 0
RETAIL 49 |  | 87.03 | 936.7909 |  | 0
RETAIL 50 |  | 87.03 | 936.7909 |  | 0
RETAIL 51 |  | 87.03 | 936.7909 |  | 0
RETAIL 52 |  | 87.03 | 936.7909 |  | 0
RETAIL 53 |  | 87.03 | 936.7909 |  | 0
ST 1 |  | 18.85 | 202.9014
ST 2 |  | 18.85 | 202.9014
ST 3 |  | 19.62 | 211.1897
ST 4 |  | 18.85 | 202.9014
ST 5 |  | 18.85 | 202.9014
ST 6 |  | 18.85 | 202.9014
ST 7 |  | 18.85 | 202.9014
ST 8 |  | 20.14 | 216.787
ST 9 |  | 19.92 | 214.4189
ST 10 |  | 18.85 | 202.9014
GENERATOR 1 |  | 15.55 | 167.3802
MALE TOILET 1 |  | 18.86 | 203.009
FEMALE TOILET 1 |  | 15.5 | 166.842
OKU 1 |  | 5.43 | 58.4485
TNB DOUBLE CHAMBER SUBSTATION NO 1 |  | 62.68 | 674.6875
TNB DOUBLE CHAMBER SUBSTATION NO 2 |  | 61.44 | 661.3402
TNB METER ROOM-1 |  | 5.1 | 54.8964
MSB ROOM 01 (RETAILS) |  | 23.21 | 249.8324
TNB METER ROOM-2 |  | 5.1 | 54.8964
MSB ROOM 01(STUDIO APART) |  | 28.16 | 303.1142
JANITOR 1 |  | 3.14 | 33.799
LACTATION ROOM 1 |  | 3.36 | 36.167
MALE TOILET 2 |  | 16.41 | 176.6372
FEMALE TOILET 2 |  | 15.33 | 165.0121
OKU 2 |  | 4.28 | 46.0699
MAIL ROOM RETAIL 1 |  | 7.13 | 76.7473
STUDIO APART. BLK 1 MAIL ROOM 1 |  | 11.97 | 128.8451
LIFT LOBBY 1 |  | 24.71 | 265.9784
WET RISER PUMP & TANK ROOM |  | 67.94 | 731.3062
TNB DOUBLE CHAMBER SUBSTATION NO 3 |  | 77.39 | 833.026
MSB ROOM 02 |  | 34.22 | 368.3441
STUDIO APART. BLK 1 MAIL ROOM 2 |  | 15.92 | 171.3629
MAIL ROOM RETAIL 2 |  | 6.69 | 72.0112
LACTATION ROOM 2 |  | 4 | 43.056
OKU 3 |  | 6.1 | 65.6604
FEMALE TOILET 3 |  | 12.22 | 131.5361
MALE TOILET 3 |  | 15.64 | 168.349
LIFT LOBBY 2 |  | 24.38 | 262.4263
OKU 4 |  | 5.03 | 54.1429
LACTATION 4 |  | 6.48 | 69.7507
MALE TOILET 4 |  | 13.48 | 145.0987
FEMALE TOILET 4 |  | 15.48 | 166.6267
TNB DOUBLE CHAMBER SUBSTATION NO 4 |  | 65.68 | 706.9795
TNB SINGLE CHAMBER SUBSTATION NO 5 |  | 43.18 | 464.7895
TNB METER ROOM-3 |  | 4 | 43.056
MSB ROOM 3 |  | 51.37 | 552.9467
CONTAINER ROOM |  | 71.88 | 773.7163
FAN & PANEL ROOM |  | 28.58 | 307.6351
FIRE CONTROL ROOM |  | 44.44 | 478.3522
GENERATOR 2 |  | 28 | 301.392
MDF ROOM |  | 18 | 193.752
LEVEL 2
RETAIL 1 |  | 213.46 | 2297.6834 |  | 0
RETAIL 2 |  | 281.23 | 3027.1597 |  | 0
RETAIL 3 |  | 90.48 | 973.9267 |  | 0
RETAIL 3A |  | 87.36 | 940.343 |  | 0
RETAIL 5 |  | 87.36 | 940.343 |  | 0
RETAIL 6 |  | 87.36 | 940.343 |  | 0
RETAIL 7 |  | 58.76 | 632.4926 |  | 0
RETAIL 8 |  | 87.36 | 940.343 |  | 0
RETAIL 9 |  | 154.9 | 1667.3436 |  | 0
RETAIL 10 |  | 154.9 | 1667.3436 |  | 0
RETAIL 11 |  | 154.9 | 1667.3436 |  | 0
RETAIL 12 |  | 153.81 | 1655.6108 |  | 0
RETAIL 12A |  | 152.07 | 1636.8815 |  | 0
RETAIL 12B |  | 144.22 | 1552.3841 |  | 0
RETAIL 15 |  | 144.22 | 1552.3841 |  | 0
RETAIL 16 |  | 128.2 | 1379.9448 |  | 0
RETAIL 17 |  | 100.74 | 1084.3654 |  | 0
RETAIL 18 |  | 144.92 | 1559.9189 |  | 0
RETAIL 19 |  | 144.92 | 1559.9189 |  | 0
RETAIL 20 |  | 146.98 | 1582.0927 |  | 0
RETAIL 21 |  | 87.2 | 938.6208 |  | 0
RETAIL 22 |  | 154.89 | 1667.236 |  | 0
RETAIL 23 |  | 154.89 | 1667.236 |  | 0
RETAIL 23A |  | 149.55 | 1609.7562 |  | 0
RETAIL 25 |  | 60.6 | 652.2984 |  | 0
RETAIL 26 |  | 86.88 | 935.1763 |  | 0
RETAIL 27 |  | 154.9 | 1667.3436 |  | 0
RETAIL 28 |  | 161.8 | 1741.6152 |  | 0
RETAIL 29 |  | 161.81 | 1741.7228 |  | 0
RETAIL 30 |  | 154.9 | 1667.3436 |  | 0
RETAIL 31 |  | 154.9 | 1667.3436 |  | 0
RETAIL 32 |  | 87.36 | 940.343 |  | 0
RETAIL 33 |  | 87.36 | 940.343 |  | 0
RETAIL 33A |  | 58.76 | 632.4926 |  | 0
RETAIL 35 |  | 87.36 | 940.343 |  | 0
RETAIL 36 |  | 87.36 | 940.343 |  | 0
RETAIL 37 |  | 87.36 | 940.343 |  | 0
RETAIL 38 |  | 159.42 | 1715.9969 |  | 0
RETAIL 39 |  | 89.56 | 964.0238 |  | 0
RETAIL 40 |  | 87.36 | 940.343 |  | 0
RETAIL 41 |  | 87.36 | 940.343 |  | 0
RETAIL 42 |  | 87.36 | 940.343 |  | 0
RETAIL 43 |  | 87.36 | 940.343 |  | 0
RETAIL 43A |  | 87.36 | 940.343 |  | 0
RETAIL 45 |  | 87.78 | 944.8639 |  | 0
RETAIL 46 |  | 46.06 | 495.7898 |  | 0
RETAIL 47 |  | 90.9 | 978.4476 |  | 0
RETAIL 48 |  | 90.9 | 978.4476 |  | 0
RETAIL 49 |  | 87.03 | 936.7909 |  | 0
RETAIL 50 |  | 66.8 | 719.0352 |  | 0
RETAIL 51 |  | 59.11 | 636.26 |  | 0
RETAIL 52 |  | 84.02 | 904.3913 |  | 0
RETAIL 53 |  | 87.02 | 936.6833 |  | 0
RETAIL 53A |  | 87.02 | 936.6833 |  | 0
RETAIL 55 |  | 48.17 | 518.5019 |  | 0
RETAIL 56 |  | 73.73 | 793.6297 |  | 0
RETAIL 57 |  | 72.7 | 782.5428 |  | 0
RETAIL 58 |  | 72.7 | 782.5428 |  | 0
RETAIL 59 |  | 50.54 | 544.0126 |  | 0
RETAIL 60 |  | 86.65 | 932.7006 |  | 0
RETAIL 61 |  | 97.7 | 1051.6428 |  | 0
RETAIL 62 |  | 97.7 | 1051.6428 |  | 0
RETAIL 63 |  | 120.96 | 1302.0134 |  | 0
RETAIL 63A |  | 83.35 | 897.1794 |  | 0
RETAIL 65 |  | 87.02 | 936.6833 |  | 0
RETAIL 66 |  | 87.02 | 936.6833 |  | 0
RETAIL 67 |  | 87.02 | 936.6833 |  | 0
RETAIL 68 |  | 87.36 | 940.343 |  | 0
RETAIL 69 |  | 87.36 | 940.343 |  | 0
RETAIL 70 |  | 87.36 | 940.343 |  | 0
RETAIL 71 |  | 87.36 | 940.343 |  | 0
RETAIL 72 |  | 90.48 | 973.9267 |  | 0
LEVEL 3
RETAIL 1 |  | 213.46 | 2297.6834 |  | 0
RETAIL 2 |  | 281.23 | 3027.1597 |  | 0
RETAIL 3 |  | 160.43 | 1726.8685 |  | 0
RETAIL 3A |  | 154.9 | 1667.3436 |  | 0
RETAIL 5 |  | 154.9 | 1667.3436 |  | 0
RETAIL 6 |  | 87.36 | 940.343 |  | 0
RETAIL 7 |  | 58.76 | 632.4926 |  | 0
RETAIL 8 |  | 87.36 | 940.343 |  | 0
RETAIL 9 |  | 87.36 | 940.343 |  | 0
RETAIL 10 |  | 87.36 | 940.343 |  | 0
RETAIL 11 |  | 87.36 | 940.343 |  | 0
RETAIL 12 |  | 153.81 | 1655.6108 |  | 0
RETAIL 12A |  | 152.07 | 1636.8815 |  | 0
RETAIL 12B |  | 144.22 | 1552.3841 |  | 0
RETAIL 15 |  | 144.22 | 1552.3841 |  | 0
RETAIL 16 |  | 128.22 | 1380.1601 |  | 0
RETAIL 17 |  | 100.74 | 1084.3654 |  | 0
RETAIL 18 |  | 144.92 | 1559.9189 |  | 0
RETAIL 19 |  | 144.92 | 1559.9189 |  | 0
RETAIL 20 |  | 146.98 | 1582.0927 |  | 0
RETAIL 21 |  | 87.2 | 938.6208 |  | 0
RETAIL 22 |  | 154.89 | 1667.236 |  | 0
RETAIL 23 |  | 154.9 | 1667.3436 |  | 0
RETAIL 23A |  | 149.55 | 1609.7562 |  | 0
RETAIL 25 |  | 60.6 | 652.2984 |  | 0
RETAIL 26 |  | 86.88 | 935.1763 |  | 0
RETAIL 27 |  | 154.9 | 1667.3436 |  | 0
RETAIL 28 |  | 161.81 | 1741.7228 |  | 0
RETAIL 29 |  | 109.69 | 1180.7032 |  | 0
RETAIL 30 |  | 87.36 | 940.343 |  | 0
RETAIL 31 |  | 87.36 | 940.343 |  | 0
RETAIL 32 |  | 87.36 | 940.343 |  | 0
RETAIL 33 |  | 87.36 | 940.343 |  | 0
RETAIL 33A |  | 58.76 | 632.4926 |  | 0
RETAIL 35 |  | 154.9 | 1667.3436 |  | 0
RETAIL 36 |  | 154.9 | 1667.3436 |  | 0
RETAIL 37 |  | 154.9 | 1667.3436 |  | 0
RETAIL 38 |  | 159.42 | 1715.9969 |  | 0
RETAIL 39 |  | 89.56 | 964.0238 |  | 0
RETAIL 40 |  | 87.02 | 936.6833 |  | 0
RETAIL 41 |  | 87.02 | 936.6833 |  | 0
RETAIL 42 |  | 87.02 | 936.6833 |  | 0
RETAIL 43 |  | 87.36 | 940.343 |  | 0
RETAIL 43A |  | 87.36 | 940.343 |  | 0
RETAIL 45 |  | 87.77 | 944.7563 |  | 0
RETAIL 46 |  | 66.34 | 714.0838 |  | 0
RETAIL 47 |  | 90.9 | 978.4476 |  | 0
RETAIL 48 |  | 87.03 | 936.7909 |  | 0
RETAIL 49 |  | 66.8 | 719.0352 |  | 0
RETAIL 50 |  | 59.11 | 636.26 |  | 0
RETAIL 51 |  | 84.02 | 904.3913 |  | 0
RETAIL 52 |  | 87.02 | 936.6833 |  | 0
RETAIL 53 |  | 87.02 | 936.6833 |  | 0
RETAIL 53A |  | 48.17 | 518.5019 |  | 0
RETAIL 55 |  | 73.74 | 793.7374 |  | 0
RETAIL 56 |  | 72.7 | 782.5428 |  | 0
RETAIL 57 |  | 72.7 | 782.5428 |  | 0
RETAIL 58 |  | 50.54 | 544.0126 |  | 0
RETAIL 59 |  | 86.65 | 932.7006 |  | 0
RETAIL 60 |  | 97.7 | 1051.6428 |  | 0
RETAIL 61 |  | 97.7 | 1051.6428 |  | 0
RETAIL 62 |  | 120.95 | 1301.9058 |  | 0
RETAIL 63 |  | 83.35 | 897.1794 |  | 0
RETAIL 63A |  | 87.36 | 940.343 |  | 0
RETAIL 65 |  | 87.36 | 940.343 |  | 0
RETAIL 66 |  | 87.36 | 940.343 |  | 0
RETAIL 67 |  | 87.36 | 940.343 |  | 0
RETAIL 68 |  | 87.36 | 940.343 |  | 0
RETAIL 69 |  | 87.02 | 936.6833 |  | 0
RETAIL 70 |  | 87.02 | 936.6833 |  | 0
RETAIL 71 |  | 90.13 | 970.1593 |  | 0
MANAGEMENT OFFICE |  | 43.82 | 471.6785 |  | 0
MALE SURAU |  | 16.05 | 172.7622 |  | 0
FEMALE SURAU |  | 19.11 | 205.7 |  | 0
LEVEL 4
CAR PARK - Retails |  | 7435 | 80030.34 |  | 0
CAR PARK - Studio |  | 4065 | 43755.66 |  | 0
LEVEL 5
CAR PARK - Retails |  | 3780 | 40687.92 |  | 0
CAR PARK - Studio |  | 7750 | 83421
LEVEL 6
CAR PARK - Retails |  | 3780 | 40687.92 |  | 0
CAR PARK - Studio |  | 7750 | 83421
LEVEL 7
CAR PARK - Retails |  | 3780 | 40687.92 |  | 0
CAR PARK - Studio |  | 7750 | 83421
LEVEL 8
CAR PARK |  | 11450 | 123247.8 |  | 0
LEVEL 9
FUNCTION AREA |  | 129.65 | 1395.5526 |  | 0
SWIMMING POOL |  | 452.27 | 4868.2343
CORRIDOR BLOCK A |  | 114.36 | 1230.971
CORRIDOR BLOCK B |  | 114.36 | 1230.971
LOBBY BLOCK A |  | 19.6 | 210.9744
LOBBY BLOCK B |  | 19.6 | 210.9744
STAIRCASE 4 BLOCK A |  | 16.35 | 175.9914
STAIRCASE 5 BLOCK A |  | 14 | 150.696
STAIRCASE 6 BLOCK B |  | 16.35 | 175.9914
STAIRCASE 7 BLOCK B |  | 14 | 150.696
CORRIDOR BLOCK CENTER |  | 62.86 | 676.625
LEVEL 10
OPEN DECK GARDEN |  | 187.3 | 2016.0972
GYMNASIUM |  | 139.93 | 1506.2065
CORRIDOR BLOCK A |  | 114.36 | 1230.971
CORRIDOR BLOCK B |  | 114.36 | 1230.971
LOBBY BLOCK A |  | 19.6 | 210.9744
LOBBY BLOCK B |  | 19.6 | 210.9744
STAIRCASE 4 BLOCK A |  | 16.35 | 175.9914
STAIRCASE 5 BLOCK A |  | 14 | 150.696
STAIRCASE 6 BLOCK B |  | 16.35 | 175.9914
STAIRCASE 7 BLOCK B |  | 14 | 150.696
LEVEL 11-26
CORRIDOR BLOCK A |  | 114.36 | 1230.971
CORRIDOR BLOCK B |  | 114.36 | 1230.971
LOBBY BLOCK A |  | 19.6 | 210.9744
LOBBY BLOCK B |  | 19.6 | 210.9744
STAIRCASE 4 BLOCK A |  | 16.35 | 175.9914
STAIRCASE 5 BLOCK A |  | 14 | 150.696
STAIRCASE 6 BLOCK B |  | 16.35 | 175.9914
STAIRCASE 7 BLOCK B |  | 14 | 150.696

## Sheet2
Notes:-
ROOM ILLUMINATION LEVEL
GENERAL BUILDING AREAS | MS 1525 2007 LUX RECOMMENDATION
Minimum Service illuminence | 20
Interior Walkway & Carpark | 100
Hotel Bedroom | 100
Lift Interior | 100
Corridor, Passageways, Stairs | 100
Escalator, Travellator | 150
Entrance & Exit | 100
Staff changing room, locker and cleaner room, cloak room, lavatories, stores | 100
Entrance hall, lobbies, waiting room | 100
Inquiry Desk | 300
Gate House | 200
Infrequent reading and writing | 200
General office, shops and stores, reading and writing | 300 - 400
Drawing Office | 300 - 400
Restroom | 150
Restaurant, Canteen, Cafeteria | 200
Kitchen | 150 - 300
Lounge | 150
Bathroom | 100
Toilet | 100
Bedroom | 100
Class room, Library | 300 - 500
Shop / Supermarket / Deparment store | 200 - 750
Museum and gallery | 300
Proof reading | 500
Excating Drawing | 1000
Detailed and precise work | 2000